RS485 device No in BCD code:
RS485 connection
 between BMM485 module
 in switchboard and
 TTCS concentrator with
FTP 5E AWG24 cable.
1
5
pin1 -24V blue+brown
pin2 +24V w/bl+w/br
pin3 shield shield
pin4 shield n.c.
pin5 - in/outRS485 n.c.
pin6 +in/outRS485 n.c.
pin7 -in/outRS485 w/or+w/gr
pin8 -in/outRS485 orange+green
2
6
Please following the setting of the
 concentrator, before the final closing
of the lid, remove the packet of silica gel
 pouch and Integrate your free volume
 inside the concentrator.
 Please post any opening replace
 the silica gel with a new one.
3
8
4
9
BMM485 module
-24V
+24V
RS485+
shield
RS485-
con.2
cable FTP 5E AWG24
RS485-
RS485+
shield
Con.1 and con.2 is equivalent.
+24V
con.1
-24V
switch 1, 2 = ON : RS485
switch 1, 2 = OFF: RS232