RS485 device No in BCD code:
RS485 connection
between BMM485 module
 in switchboard and
 TTCS concentrator with
 Li2YCYv (TP) 2x2x0.34 cable.
1
5
pin1 -24V brown
pin2 +24V white
pin3 shield shield
pin4 shield n.c.
pin5 - in/outRS485 n.c.
pin6 +in/outRS485 n.c.
pin7 -in/outRS485 yellow
pin8 -in/outRS485 green
2
6
3
8
Please following the setting of the concentrator,
 before the final closing of the lid, remove the
 packet of silica gel pouch and Integrate your
 free volume inside the concentrator.
 Please post any opening replace the silica gel
with a new one.
4
9
BMM485 module
-24V
RS485+
+24V
shield
RS485-
-RS485
con.2
+RS485
Con.1 and con.2
 is equivalent.
shield
con.1
+24V
-24V
switch 1, 2 = ON : RS485
switch 1, 2 = OFF: RS232